## Slide 1
AIR CONDITIONING · CHAPTER 1
1.3 Vapor Compression Refrigeration Cycle
Latent heat, four components, P-h diagram, and COP
A visual-led lecture deck for concept-first teaching and engineering discussion.
Latent heat
Compressor
P-h diagram
COP
1.3
1
2
3
4
From components → decisions → engineering judgement
Air Conditioning · Chapter 1 · Topic 1.3
1

## Slide 2
Latent heat is the basis of refrigeration
Phase change moves large amounts of heat at nearly constant temperature.
2
Air Conditioning · Chapter 1 · Topic 1.3
2
THERMODYNAMIC FOUNDATION
Cooling comes from evaporation
1
Evaporation
refrigerant absorbs heat indoors
2
Condensation
refrigerant rejects heat outdoors
3
Boiling point
set by refrigerant pressure
Latent heat: heat transfer during phase change

## Slide 3
The cycle has four components
Each component performs one thermodynamic function.
3
Air Conditioning · Chapter 1 · Topic 1.3
3
CLOSED LOOP
Pressure and phase are controlled in sequence
1
Compressor
raises pressure and temperature
2
Condenser
rejects heat; vapor → liquid
3
Expansion device
drops pressure and temperature
Four-component refrigeration loop

## Slide 4
Four processes repeat continuously
The same loop can be read as thermodynamic processes.
4
Air Conditioning · Chapter 1 · Topic 1.3
4
PROCESS MAP
1→2→3→4→1
1
1→2 Compression
pressure rises; work input
2
2→3 Condensation
heat rejected at high pressure
3
3→4 Expansion
throttling; pressure drops
Four processes of the vapor compression cycle

## Slide 5
The P-h diagram turns the cycle into numbers
Enthalpy differences give capacity, work, and heat rejection.
5
Air Conditioning · Chapter 1 · Topic 1.3
5
P-H READING
Horizontal axis is enthalpy; vertical axis is pressure
1
Refrigerating effect
h1 − h4
2
Compressor work
h2 − h1
3
Condenser rejection
h2 − h3
Pressure–enthalpy diagram with cycle path

## Slide 6
COP measures cooling per input energy
Higher COP means less electrical power for the same cooling.
6
Air Conditioning · Chapter 1 · Topic 1.3
6
EFFICIENCY METRIC
COP = useful cooling ÷ compressor input
1
Typical range
about 2.5–7.5 by system and condition
2
EER link
EER = COP × 3.412
3
Temperature lift
higher condensing temperature lowers COP
Typical COP ranges for vapor compression systems

## Slide 7
Topic 1.3 summary
What students should remember
7
Air Conditioning · Chapter 1 · Topic 1.3
7
1
Latent heat moves heat
Evaporation absorbs; condensation rejects
2
Four components form the loop
compressor → condenser → expansion → evaporator
3
P-h diagram quantifies performance
read effect, work, heat rejection, and COP