## Slide 1
AIR CONDITIONING · CHAPTER 1
1.5 Refrigerants
Types, properties, environmental impact, and regulation
Refrigerant choice is both a thermodynamic and environmental design decision.
ODP
GWP
Safety
Regulation
1.5
1
2
3
4
Concept-first slides with teaching detail in the card
Air Conditioning · Chapter 1 · Topic 1.5
1

## Slide 2
The refrigerant is the heat-transfer working fluid
It absorbs heat indoors and rejects heat outdoors.
2
Air Conditioning · Chapter 1 · Topic 1.5
2
CYCLE ROLE
The working fluid carries energy around the loop
1
High latent heat
more cooling per kg
2
Practical pressure
safe pipe and equipment pressure
3
Compatibility
piping, seals, and compressor oil
Refrigerant role in the vapor compression cycle

## Slide 3
A good refrigerant is a compromise
No refrigerant is perfect in every category
3
Air Conditioning · Chapter 1 · Topic 1.5
3
1
Thermodynamic
high latent heat and good pressure curve
2
Safety
low toxicity and flammability for occupied spaces
3
Materials
does not corrode or degrade oil/seals
4
Environment
zero ODP and low GWP
5
Serviceability
available tools, cylinders, and technician skill

## Slide 4
ODP and GWP are different environmental risks
Zero ozone depletion does not guarantee low climate impact.
4
Air Conditioning · Chapter 1 · Topic 1.5
4
INDICES
ODP protects ozone; GWP protects climate
1
ODP
referenced to R-11 = 1.0
2
GWP
referenced to CO₂ = 1
3
Modern target
ODP = 0 and low GWP
ODP and GWP comparison

## Slide 5
Refrigerant families changed because rules changed
Environmental regulation reshaped HVAC equipment.
5
Air Conditioning · Chapter 1 · Topic 1.5
5
EVOLUTION
CFC → HCFC → HFC → HFO/natural
1
CFC
high ODP; banned legacy
2
HCFC
lower ODP; phase-out
3
HFC
zero ODP but high GWP
Historical evolution of refrigerant families

## Slide 6
Common families: what students should say aloud
Turn the table into engineering judgement
6
Air Conditioning · Chapter 1 · Topic 1.5
6
1
CFC
legacy only; severe ozone issue
2
HCFC
R-22 style transition refrigerant; phase-out risk
3
HFC
common today but climate phase-down pressure
4
HFO
low GWP; often A2L and higher cost
5
Natural
very low GWP; toxicity/pressure/flammability constraints

## Slide 7
Thailand must design for phase-out and phase-down
Equipment life is longer than many refrigerant policy milestones.
7
Air Conditioning · Chapter 1 · Topic 1.5
7
REGULATION
Specify for the future, not only today
1
HCFC phase-out
near-complete by 2040
2
HFC phase-down
started 2024; target reduction by 2045
3
Design implication
future availability and price risk
Thailand refrigerant regulation timeline

## Slide 8
Safety class affects room and service design
Low-GWP choices may introduce mild flammability or pressure issues
8
Air Conditioning · Chapter 1 · Topic 1.5
8
1
A1
lower toxicity, no flame propagation
2
A2L
mildly flammable; check charge and ventilation
3
A3
flammable; usually small sealed systems
4
CO₂
very high pressure; special equipment
5
Ammonia
excellent performance but toxic; industrial controls

## Slide 9
Refrigerant selection is a multi-criteria decision
Do not choose only by COP or only by GWP.
9
Air Conditioning · Chapter 1 · Topic 1.5
9
SELECTION LOGIC
Balance performance, safety, environment, and service
1
Efficiency
cycle performance and pressure levels
2
Safety
toxicity, flammability, charge limits
3
Regulation
future availability and compliance
Refrigerant selection factors

## Slide 10
Pause question: R-410A or R-32 for a new split AC?
Use this to make students compare more than one criterion
10
Air Conditioning · Chapter 1 · Topic 1.5
10
1
R-410A
widely used; high GWP ≈ 2088
2
R-32
lower GWP ≈ 675
3
Safety
R-32 is A2L mildly flammable
4
Answer
prefer lower GWP when approved equipment and service support exist

## Slide 11
Topic 1.5 — what students should remember
11
Air Conditioning · Chapter 1 · Topic 1.5
11
1
Refrigerants affect many risks
efficiency, safety, service, environment, and regulation
2
ODP and GWP are separate
zero ODP is not enough if GWP remains high
3
Specification is long-term
choose for service life and regulatory trajectory