## Slide 1
AIR CONDITIONING · CHAPTER 1
1.6 Types of AC Systems and System Selection
Capacity units, system families, comparison, and selection workflow
30-minute visual lecture deck: concept → engineering judgement → quick check.
TR/Btu/h/kW
Split
VRF
Chilled water
1.6
Enough detail for discussion, examples, and Q&A
Air Conditioning · Chapter 1 · Topic 1.6
1

## Slide 2
Learning outcomes for a 30-minute lecture
Students should connect building needs to system type
2
Air Conditioning · Chapter 1 · Topic 1.6
2
1
Convert capacity units
TR, Btu/h, and kW
2
Classify systems
window, split, package, VRF, chilled water
3
Compare trade-offs
cost, zoning, efficiency, service life
4
Apply selection logic
choose based on building constraints
5
Discuss Thai context
climate, operation hours, maintenance capability

## Slide 3
Cooling capacity uses three common units
Catalogues and standards may use different unit systems.
3
Air Conditioning · Chapter 1 · Topic 1.6
3
CAPACITY UNITS
1 TR = 12,000 Btu/h = 3.517 kW
1
TR
ton of refrigeration
2
Btu/h
common in room AC catalogues
3
kW
SI engineering calculation unit
Cooling capacity unit relationship

## Slide 4
Preliminary sizing: use only as a first-pass check
Rule-of-thumb values are not a substitute for load calculation
4
Air Conditioning · Chapter 1 · Topic 1.6
4
1
Residential
about 300–400 Btu/h·m²
2
Office
about 500–600 Btu/h·m²
3
Restaurant
about 600–800 Btu/h·m²
4
Department store
about 700–900 Btu/h·m²
5
Engineering caution
verify with CLTD/CLF, RTS, or accepted load method

## Slide 5
Window units are self-contained and low cost
All components are in one cabinet.
5
Air Conditioning · Chapter 1 · Topic 1.6
5
SYSTEM TYPE 1
Simple installation, limited comfort quality
1
Capacity
5,000–24,000 Btu/h
2
Strength
lowest installed cost
3
Weakness
noise, wall opening, lower efficiency
Window AC arrangement

## Slide 6
Split systems separate indoor comfort from outdoor heat rejection
Moving compressor outdoors improves acoustic comfort.
6
Air Conditioning · Chapter 1 · Topic 1.6
6
SYSTEM TYPE 2
Most common small-building solution
1
Indoor unit
evaporator and indoor fan
2
Outdoor unit
compressor and condenser
3
Applications
homes, condos, small offices
Split system configuration

## Slide 7
Package units condition one large airflow
A single cabinet feeds ductwork for a large zone.
7
Air Conditioning · Chapter 1 · Topic 1.6
7
SYSTEM TYPE 3
Useful for open-plan buildings
1
Capacity
about 2–25 TR
2
Strength
single location, central maintenance
3
Weakness
duct energy, roof load, zone control complexity
Package unit with duct distribution

## Slide 8
VRF systems serve many zones with refrigerant flow control
One outdoor system meters refrigerant to many indoor units.
8
Air Conditioning · Chapter 1 · Topic 1.6
8
SYSTEM TYPE 4
High zoning flexibility without a chiller plant
1
Zoning
independent IDU setpoints
2
Inverter
capacity modulates to load
3
Watchout
leak testing, cost, proprietary controls
VRF/VRV system configuration

## Slide 9
Chilled water systems dominate large buildings
Refrigerant stays in the chiller; water distributes cooling.
9
Air Conditioning · Chapter 1 · Topic 1.6
9
SYSTEM TYPE 5
Best where scale and lifecycle efficiency justify first cost
1
High efficiency
especially water-cooled chillers
2
Scalable
multiple chillers/AHUs/FCUs
3
Watchout
plant room, pumps, tower, skilled operation
Chilled water system circuit

## Slide 10
System comparison matrix
Fast screening for design discussion
10
Air Conditioning · Chapter 1 · Topic 1.6
10
System
Typical scale
Strength
Main limitation
Window
one small room
lowest first cost
noise / envelope opening
Split
room to small office
quiet, flexible
many outdoor units
Package
large single zone
central cabinet
duct loss / roof load
VRF
multi-room mid-scale
zone control
cost + specialist service
Chilled water
large buildings
efficiency + redundancy
highest capital complexity

## Slide 11
System selection is a trade-off, not a lookup table
The best system depends on building operation and constraints.
11
Air Conditioning · Chapter 1 · Topic 1.6
11
SELECTION FRAMEWORK
Evaluate lifecycle, not only first cost
1
Load and scale
capacity and operating schedule
2
Zoning
single zone vs many independent rooms
3
Budget
capital vs operating cost
Comparative overview of system types

## Slide 12
Worked selection scenarios
Ask students to justify, not memorize
12
Air Conditioning · Chapter 1 · Topic 1.6
12
1
Small bedroom
split AC: quiet and flexible
2
Temporary site office
window or small split: low first cost
3
Single-story retail hall
package unit: central ducted solution
4
Boutique hotel
VRF/FCU: room-by-room control
5
Hospital or mall
chilled water: efficiency, filtration, redundancy

## Slide 13
Pause question: 20-story mixed-use tower
Retail + offices + hotel suites in one building
13
Air Conditioning · Chapter 1 · Topic 1.6
13
1
Retail floors
AHU/package/chilled water airside for open zones
2
Office floors
AHU/VAV or chilled water terminals
3
Hotel suites
FCU or VRF for individual room control
4
Fresh air
separate AHU/DOAS often needed
5
Final answer
hybrid systems are common in real buildings

## Slide 14
Topic 1.6 summary
What students should remember for design conversations
14
Air Conditioning · Chapter 1 · Topic 1.6
14
1
Capacity units must be fluent
TR, Btu/h, and kW describe the same heat-rate capacity
2
System type follows building scale
room units → split/VRF/package → chilled water plants
3
Selection is multi-criteria
zoning, cost, efficiency, service life, and maintenance